## locations
dbo.section | dbo.entity_name | dbo.type | dbo.connections.contains
Buildings | IN-GUR-SIGD | FACILITIES/BUILDING
Floors | IN-GUR-SIGD_FL1 | FACILITIES/FLOOR | IN-GUR-SIGD
Rooms | IN-GUR-SIGD_RM1 | FACILITIES/ROOM | IN-GUR-SIGD_FL1
Zones | IN-GUR-SIGD_ZN1 | HVAC/ZONE | IN-GUR-SIGD_RM1
Rooms | IN-GUR-SIGD_RM2 | FACILITIES/ROOM | IN-GUR-SIGD_ZN1
Zones | IN-GUR-SIGD_ZN2 | HVAC/ZONE | IN-GUR-SIGD_RM2

## assets
entity_instance_name | udmi.version | udmi.timestamp | udmi.system.location.site | udmi.system.location.section | udmi.system.location.position.x | udmi.system.location.position.y | udmi.system.location.position.z | udmi.physical_tag.asset.guid | udmi.physical_tag.asset.site | udmi.physical_tag.asset.name | udmi.pointset.points | udmi.cloud.auth_type | dbo.devices_or_virtual_devices | dbo.type | dbo.cloud_device_id | dbo.connections.feeds | dbo.connections.controls | dbo.links | dbo.links.points | Location | Reporting Device
EM-01 | 1 | 2020-12-08T09:03:43Z | IN-GUR-SIGD | IN-GUR-SIGD | 10 | 10 | 10 | 26rmarOMz9ZOgBkt9da8MC | EM-01 | EM-01 | EM-01 | RS256 | Device | HVAC/EM_PWM_AVCM_PVCM | 1234 |  |  |  | EM-01 | BSMT-01 | HLI-25

## device_entities
points_type | udmi.pointset.points | udmi.pointset.units | dbo.states | dbo.translation.fields | dbo.translation.units | dbo.abstracts
EM-01 | average_inter_line_voltage_sensor | volts |  | average_inter_line_voltage_sensor | volts:"V"
EM-01 | average_line_neutral_voltage_sensor | volts |  | average_line_neutral_voltage_sensor | volts:"V"
EM-01 | average_line_current_sensor | amperes |  | average_line_current_sensor | amperes:"A"
EM-01 | line_frequency_sensor | hertz |  | line_frequency_sensor | hertz:"Hz"
EM-01 | power_sensor | kilowatts |  | power_sensor | kilowatts:"kW"
EM-01 | energy_accumulator | kilowatt_hours |  | energy_accumulator | kilowatt_hours:"kW-hrs"
EM-01 | apparent_power_sensor | kilovolt_amperes_apparent |  | apparent_power_sensor | kilovolt_amperes_apparent:”KV”
EM-01 | apparent_energy_accumulator | kilovolt_amperes_apparent_hours |  | apparent_energy_accumulator | kilovolt_amperes_apparent_hours:”KV”
EM-01 | reactive_energy_accumulator | kilovolt_amperes_reactive_hours |  | reactive_energy_accumulator | kilovolt_amperes_reactive_hours:”KV”
EM-01 | reactive_power_sensor | kilovolt_amperes_reactive |  | reactive_power_sensor | kilovolt_amperes_reactive:”KV”
EM-01 | powerfactor_sensor |  |  | powerfactor_sensor | x:”y”
EM-01 | phase1_line_current_sensor | amperes |  | phase1_line_current_sensor | amperes:"A"
EM-01 | phase2_line_current_sensor | amperes |  | phase2_line_current_sensor | amperes:"A"
EM-01 | phase3_line_current_sensor | amperes |  | phase3_line_current_sensor | amperes:"A"
EM-01 | phase1_phase2_line_voltage_sensor | volts |  | phase1_phase2_line_voltage_sensor | volts:"V"
EM-01 | phase2_phase3_line_voltage_sensor | volts |  | phase2_phase3_line_voltage_sensor | volts:"V"
EM-01 | phase1_phase3_line_voltage_sensor | volts |  | phase1_phase3_line_voltage_sensor | volts:"V"

## virtual_device_entities
virtual_points_type | device_points_type | dbo.source_device_field | dbo.virtual_device_field | dbo.abstracts

## asset_template
entity_instance_name | udmi.system.location.site | udmi.pointset.points | udmi.system.location.section | udmi.system.location.position.x | udmi.system.location.position.y | udmi.system.location.position.z | udmi.physical_tag.asset.guid | udmi.physical_tag.asset.site | udmi.physical_tag.asset.name | udmi.cloud.auth_type | dbo.devices_or_virtual_devices | dbo.type | dbo.connections.feeds | dbo.connections.controls | dbo.links | dbo.links.points | location | reporting_device